## running data
register	name	scale factor	read data
35100	RTC_YEAR_MONTH		5380
35101	RTC_DATE_HOUR		1036
35102	RTC_MINUTE_SECOND		798
35103	PV1 Voltage	-1	1636
35104	PV1 Current	-1	8
35105	PV1 power MSB		0
35106	PV1 power LSB		130
35107	PV2 Voltage		0
35108	PV2 Current		0
35109	PV2 power MSB		0
35110	PV2 power LSB		0
35111	PV3 Voltage		-1
35112	PV3 Current		-1
35113	PV3 power MSB		-1
35114	PV3 power LSB		-1
35115	PV4 Voltage		-1
35116	PV4 Current		-1
35117	PV4 power MSB		-1
35118	PV4 power LSB		-1
35119	PV_MODE		0
35120			2
35121	VOLTAGE_L1	-1	2318
35122	CURRENT_L1	-1	64
35123	F_GRID_R	-2	4996
35124	POWER_L1		0
35125	POWER_L1	0	1441
35126	VOLTAGE_L2		-1
35127	CURRENT_L2		-1
35128	F_GRID_S		-1
35129	POWER_L2		32767
35130	POWER_L2		-1
35131	VOLTAGE_L3		-1
35132	CURRENT_L3		-1
35133	F_GRID_T		-1
35134	POWER_L3		32767
35135	POWER_L3		-1
35136	GRID_MODE		1
35137	TOTAL_INV_POWER		0
35138	TOTAL_INV_POWER		1441
35139	AC_ACTIVE_POWER		0
35140	AC_ACTIVE_POWER		-69
35141	AC_REACTIVE_POWER		32767
35142	AC_REACTIVE_POWER		-1
35143	AC_APPARENT_POWER		-1
35144	AC_APPARENT_POWER		-1
35145	BACK_UP_V_LOAD_R		2318
35146	BACK_UP_I_LOAD_R		6
35147	BACK_UP_F_LOAD_R		4996
35148	LOAD_MODE_R		1
35149	BACK_UP_P_LOAD_R		0
35150	BACK_UP_P_LOAD_R		0
35151	BACK_UP_V_LOAD_S		-1
35152	BACK_UP_I_LOAD_S		-1
35153	BACK_UP_F_LOAD_S		-1
35154	LOAD_MODE_S		-1
35155	BACK_UP_P_LOAD_S		-1
35156	BACK_UP_P_LOAD_S		-1
35157	BACK_UP_V_LOAD_T		-1
35158	BACK_UP_I_LOAD_T		-1
35159	BACK_UP_F_LOAD_T		-1
35160	LOAD_MODE_T		-1
35161	BACK_UP_P_LOAD_T		-1
35162	BACK_UP_P_LOAD_T		-1
35163	P_LOAD_R		0
35164	P_LOAD_R		1510
35165	P_LOAD_S		-32768
35166	P_LOAD_S		0
35167	P_LOAD_T		-32768
35168	P_LOAD_T		0
35169	TOTAL_BACK_UP_LOAD		0
35170	TOTAL_BACK_UP_LOAD		0
35171	TOTAL_LOAD_POWER		0
35172	TOTAL_LOAD_POWER		1510
35173	UPS_LOAD_PERCENT		2
35174	AIR_TEMPERATURE	?	555
35175	MODULE_TEMPERATURE		32767
35176	RADIATOR_TEMPERATURE		324
35177	FUNCTION_BIT_VALUE		256
35178	BUS_VOLTAGE	-1	4150
35179	NBUS_VOLTAGE		-1
35180	V_BATTERY1		3651
35181	I_BATTERY1		37
35182	P_BATTERY1		0
35183	P_BATTERY1		1350
35184	BATTERY_MODE		2
35185	WARNING_CODE		0
35186	SAFETY_COUNTRY		37
35187	WORK_MODE		1
35188	OPERATION_MODE		-1
35189	INV_ERR_H		0
35190	INV_ERR_L		0
35191	PV_E_TOTAL		0
35192	PV_E_TOTAL		3971
35193	PV_E_DAY		0
35194	PV_E_DAY		6
35195	E_TOTAL		0
35196	E_TOTAL		4377
35197	H_TOTAL		0
35198	H_TOTAL		2380
35199	E_DAY_SELL		22
35200	E_TOTAL_BUY		0
35201	E_TOTAL_BUY		1032
35202	E_DAY_BUY		6
35203	E_TOTAL_LOAD		0
35204	E_TOTAL_LOAD		8216
35205	E_LOAD_DAY		38
35206	E_BATTERY_CHARGE		0
35207	E_BATTERY_CHARGE		3428
35208	E_CHARGE_DAY		5
35209	E_BATTERY_DISCHARGE		0
35210	E_BATTERY_DISCHARGE		2871
35211	E_DISCHARGE_DAY		16
35212	BATT_STRINGS		7
35213	CPLD_WARNING_CODE		0
35214	W_CHARGER_CTRL_FLAG		0
35215	DERATE_FLAG		0
35216	DERATE_FROZEN_POWER		0
35217	DIAG_STATUS_H		0
35218	DIAG_STATUS_L		0
35219
35220
35221
35222
35223
35224
35225
35226

## meter
register	name
36000
36001
36002
36003	B_METER_COMMUNICATE_STATUS
36004	METER_COMMUNICATE_STATUS
36005	MT_ACTIVE_POWER_R
36006	MT_ACTIVE_POWER_S
36007	MT_ACTIVE_POWER_T
36008	MT_TOTAL_ACTIVE_POWER
36009	MT_TOTAL_REACTIVE_POWER
36010	METER_PF_R
36011	METER_PF_S
36012	METER_PF_T
36013	METER_POWER_FACTOR
36014	METER_FREQUENCY

## BMS
37000		255
37001	BATTERY_TYPE_INDEX	498
37002	BMS_STATUS	1
37003	BMS_PACK_TEMPERATURE	222
37004	BMS_CHARGE_IMAX	2
37005	BMS_DISCHARGE_IMAX	25
37006	BMS_ERR	0
37007	SOC	80
37008	SOH	85
37009	BMS_BATTERY_STRINGS	7
37010	BMS_WARN	0
37011	BATTERY_PROTOCOL	286

## battery control
register	name	scale	read data
47500	STOP_SOC_PROTECT		0
47501	BATTERY_FLOAT_VOLT		3843
47502	BATTERY_FLOAT_CURRENT		30
47503	BATTERY_FLOAT_TIME		30
47504	BATTERY_TYPE_INDEX_ARM		498
47505	MANUFACTURE_CODE		10
47506	DC_VOLT_OUTPUT		0
47507	BAT_AVG_CHG_VOLT		4025
47508	BAT_AVG_CHG_HOURS		0
47509	FEED_POWER_ENABLE		1
47510	FEED_POWER_PARA		0
47511	EMS_POWER_MODE		1
47512	EMS_POWER_SET		0
47513	BAT_BMS_CURR_LMT_COFF		1
47514	BATTERY_PROTOCOL_ARM		286
47515	START_TIME_1		0
47516	END_TIME_1		1536
47517	BAT_POWER_PERCENT_1		-80
47518			127
47519	START_TIME_2		1536
47520	END_TIME_2		5632
47521	BAT_POWER_PERCENT_2		80
47522			127
47523	START_TIME_3		5888
47524	END_TIME_3		5947
47525	BAT_POWER_PERCENT_3		0
47526			127
47527	START_TIME_4		12288
47528	END_TIME_4		12288
47529	BAT_POWER_PERCENT_4		0
47530			0
47531	SOC_START_TO_FORCE_CHARGE		50
47532	SOC_STOP_TO_FORCE_CHARGE		100
47533	CLEAR_ALL_ECONOMIC_MODE		0
47534			1
47535			0
47536			0
47537			0
47538			0
47539			4
47540			0